## Requirements
TECHNICAL REQUIREMENTS
Component | Requirement
Solar PV Capacity | 5 kWp per site
Solar Panel Rating | 410 Wp per module
Panel Type | Monocrystalline, IEC certified
System Configuration | Grid-connected with battery backup (hybrid)
Inverter Rating | 5 kVA, MPPT in-built
Inverter Capability | Must support upto 60 V battery system
Battery Type | Lead-acid GEL
Battery Rating | 150 Ah per unit
Battery Sizing | Must cover essential site loads during outages
Mounting Structure | Suitable for RCC / metal-sheet roof
DC Protection | DC isolator, DC MCB, DC SPD
AC Protection | AC MCB, AC isolator, AC SPD
Earthing | Complete earthing & grounding system
Compliance | Nepal standards, SWC & DFAT guidelines

## BoQ
Bill of Quantities
S.N. | Item Description | Specification | Unit | Qty | Unit Rate (NPR) | Total (NPR)
1 | Solar PV Modules | 410 Wp mono crystalline | Nos
2 | Solar Inverter | 5 kVA, 60 V battery capable, MPPT | No | 1
3 | GEL Battery | 150 Ah | Nos
4 | Mounting Structure | Roof mount (RCC/metal) | Set | 1
5 | DC Cables & MC4 | Complete set | Lot | 1
6 | AC Cables | Complete set | Lot | 1
7 | DC Protection Devices | MCB, SPD, isolator | Lot | 1
8 | AC Protection Devices | MCB, SPD, isolator | Lot | 1
9 | Junction / Combiner Box | Complete | Lot | 1
10 | Earthing & Lightning | Complete system | Lot | 1
11 | Transportation | To site | Job | 1
12 | Installation & Commissioning | Complete | Job | 1
Net Total (A)
Vatable Amount
13% VAT (B)
Grand Total (A+B)
Note:
Required per site

## Load 1
Emergency Equipment in Katunjebesi Health Post
Components | Quantity | Kilowatt (kW) | Usage (h/day) | Energy Consumption(kWh/day)
Vaccine Refrigerator | 1 | 0.0458 | 24 | 1.0992
Light | 8 | 0.015 | 6 | 0.72
Light | 10 | 0.01 | 5 | 0.5
Heater | 1 | 1.2 | 4 | 4.8
Electric Blanket | 4 | 0.05 | 6 | 1.2
Non-Emergency Equipment in Katunjebesi Health Post
Components | Quantity | Kilowatt | Usage (h/day) | Energy Consumption(kWh/day)
(kW)
Fan | 1 | 0.05 | 3 | 0.15
Printer | 1 | 0.72 | 1.5 | 1.08
Laptop | 3 | 0.07 | 7 | 1.47
Charger | 3 | 0.006 | 3 | 0.054
Water Dispenser | 1 | 0.55 | 5 | 2.75

## Load 2
Emergency Equipment in Sipali Birthing Center
| Components | Quantity | Kilowatt(kW) | Usage (h/day) | Energy Consumption(kWh/day)
| Vaccine Refrigerator | 1 | 0.138 | 24 | 3.312
| Baby warmer | 1 | 0.65 | 3 | 1.95
| Lights | 10 | 0.015 | 3 | 0.45
| Oxygen concentrator | 2 | 0.65 | 3 | 3.9
| Suction machine | 1 | 0.18 | 0.3 | 0.054
Non-Emergency Equipment in Sipali Birthing Center
| Components | Quantity | Kilowatt(kW) | Usage (h/day) | Energy Consumption(kWh/day)
| Air-conditioner | 1 | 1.43 | 4 | 5.72
| Washing machine | 1 | 1.95 | 1.5 | 2.925
| Television | 1 | 0.035 | 5 | 0.175
| Charger | 1 | 0.006 | 3 | 0.018
| Electric Kettle | 1 | 1.5 | 1.5 | 2.25
| Heater | 2 | 1.2 | 5 | 12
| Electric Blanket | 5 | 0.05 | 6 | 1.5

## Load 3
Emergency Equipment in Mangaltar Birthing Center
| Components | Quantity | Kilowatt(kW) | Usage (h/day) | Energy Consumption(kWh/day)
| Baby Warmer | 2 | 0.67 | 3 | 4.02
| Vaccine refrigerator | 1 | 0.138 | 24 | 3.312
| Vaccine refrigerator | 1 | 0.11 | 24 | 2.64
| Oxygen Concentrator | 2 | 0.33 | 2 | 1.32
| Suction machine | 1 | 0.18 | 3 | 0.54
| Delivery lights | 3 | 0.025 | 3 | 0.225
Non-Emergency Equipment in Mangaltar Birthing Center
| Components | Quantity | Kilowatt(kW) | Usage (h/day) | Energy Consumption(kWh/day)
| Printer | 2 | 0.69 | 3 | 4.14
| Air conditioner | 1 | 1.095 | 5 | 5.475
| Charger | 1 | 0.02 | 5 | 0.1
| Laboratory Oven | 1 | 1.5 | 1 | 1.5
| Laboratory water bath | 1 | 0.375 | 3 | 1.125
| Electric Kettle | 4 | 1.5 | 1.5 | 9
| Vaccine refrigerator | 1 | 0.0458 | 7 | 0.3206
| Heater | 2 | 1.2 | 4 | 9.6
| Electric blanket | 6 | 0.05 | 6 | 1.8